# Croghan Volunteer Fire Department

PO Box 405

Croghan, NY  13327

Annual Hose Test Best Practice

Purpose: To test all hose of the Croghan Fire Dept. by performing a visual and a pressure test to NFPA Standard 1962.

All hose in inventory will be tested annually.

Using a black marker, all hose will be marked by each coupling before the pressure test. All marks will be checked during pressure test and after to make sure that the hose does not move apart. Couplings will be visually inspected for damaged threads, corrosion, out of round couplings, loose external collars, missing lugs and damaged or missing gaskets.

Testing procedures for all hose are as follows: hose will be visually inspected, pressure tested and logged in the record book.

All hose except large diameter hose will be tested to 440psi and held for ten minutes.

The large diameter hose will be tested to 220psi and held for ten minutes.

Any hose that does not pass the visual or pressure test will be removed from service and repaired or destroyed.  All hose tested will be logged into the Hose Testing Log Book.

The hose will be identified by a letter or a number system to be able to track the hose life and performance.

Effective   06/01/2008                    By Chief Joe Aucter

reviewed 2/2014  1/2018